## Slide 1: Setting Over Current Relays on ETAP
Objectives:
To learn settings of definite time over current relays on ETAP
System used:
IEEE 4 Bus System

## Slide 2
Starting with the IEEE 4 bus system…
The additional data required in this network is grid SC MVA, which is set to 100 MVA, with X/R 17
Remove transformer from section 2 – 3 and copy line 1 in its place
Modify the load connected at bus 4 to 100 % static and 1730 kVA
Add static loads to bus 3 and 2 of 3460 and 4300 kVA respectively

## Slide 3
Run Load Flow Analysis & Note line current for all sections

## Slide 4
Run short circuit analysis:
For 3 phase fault , L-G, L-L and DLG faults & Note maximum and minimum fault currents for each bus

## Slide 5
3 phase fault

## Slide 6
L-G Fault

## Slide 7
Line-Line Fault

## Slide 8
DLG Fault

## Slide 9
Bus No | 1 | 2 | 3 | 4
Normal (A) | 427 | 427 | 232 | 79
Max If (A) | 4630 | 4000 | 3500 | 3000
Min If (A) | 4010 | 3460 | 3000 | 2450
Findings from Fault Analysis

## Slide 10
Placement of Relays and Circuit Breakers in all line sections for Over Current Protection
HV Circuit Breaker
Over current Relay
CT

## Slide 11
Circuit Breaker Ratings
Select a CB from Library, keeping in mind the interrupting capacity required.

## Slide 12
Current Transformer Ratings
Select appropriate turns ratio for CT keeping in mind the primary current in line where CT is connected. You can also select CT Burden class.

## Slide 13
Over Current Relay Parameters
Select an over current relay from a library of different models and manufacturers of OCR.

## Slide 14
For example, select Alstom P120.
To observe definite time characteristic, uncheck the instantaneous option.

## Slide 15
Connect CT with respective OCR and verify its turns ratio from Input Tab of Relay.

## Slide 16
In output Tab of Relay Editor , Add one HV CB to which the relay should send its output.

## Slide 17
Star Protective Device Coordination
Drag and Drop “Fault insertion” to any bus that you want to fault

## Slide 18
The Circuit Breaker 1 operates (indicated by a cross) when fault is placed on bus 4.